## BOILER TREAT ONE SHOT PROGRAMME
VECOM MARINE | [21 empty] | Log for low-pressure boilers BOILER TREAT ONE SHOT PROGRAMME
Recommended range:
Month / Year: |  |  |  |  | / | [13 empty] | Boiler: | [5 empty] | Primary |  |  |  | Secondary |  |  |  | Other
Vessel / IMO: | [9 empty] | / | [8 empty] | Boiler maker / Type: | [11 empty] | /
Company: | [18 empty] | Operating pressure / water capacity: | [12 empty] | /
Engineer in charge: | [18 empty] | Makeup water: | [5 empty] | Distilled |  |  |  | Shore |  |  |  | Mix
| Day: | IMPORTANT: If no measurements are taken, leave the relevant cells blank. Never make up or copy from a previous day!
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
P-alkalinity: CaCO3 (ppm) | > 300 | [31 empty] | Initial dose: 1.0 ltr / ton Mainten. dosage: 0.30 ltr / ton <100 ppm: Increase dose 25% >200 ppm: Decrease dose 10%
250 - 300
200 - 250
150 - 200
100 - 150
50 - 100
< 50
M-alkalinity | > 2*P-alkalinity
< 2*P-alkalinity
Boiler Treat One Shot ( ltr / ton ) | 1.5 - 2.0
1.0 - 1.5
0.5 - 1.0
0.3 - 0.5
< 0.3
Boiler pH | > 11.0
9.5 - 11.0
8.0 - 9.5
< 8.0
Appear- ance | Cloudy
Clear
Coloured
Chloride: Cl (ppm) | > 240 | [31 empty] | <180: Maintain daily blowdown >180: Increase daily blowdown Keep chlorides as low as possible
180 - 240
120 - 180
80 - 120
50 - 80
20 - 50
< 20
Blow down | Surface
Bottom
Oxygen Scavenger: DEHA (ppm) | > 0.8 | [31 empty] | Initial dose: 0.0225 ltr / ton 0.0225 ltr / ton will decrease oxygen by 1ppm
0.5 - 0.8
0.3 - 0.5
0.1 - 0.3
< 0.1
Hydrazide ( ltr / ton ) | 0.08 - 0.11
0.05 - 0.08
0.02 - 0.05
< 0.02
Condensate pH | > 10.5 | [31 empty] | Initial dose: 0.25 ltr / ton Daily dosage: 0.025 ltr / ton <75°C: pH 8.3-9.0 >75°C: pH 8.0-10.0
9.5 - 10.5
8.5 - 9.5
7.5 - 8.5
6.5 - 7.5
5.5 - 6.5
< 5.5
Condensate Control ( ltr / ton ) | 0.40 - 0.70
0.10 - 0.40
0.05 - 0.10
0.025 - 0.05
< 0.025
Hotwell °C | > 95°C | [31 empty] | Never add chemicals directly to the hotwell
85°C - 95°C
75°C - 85°C
< 75°C
Daily (or min. every 2 days) testing is strongly advised!
Remarks:
This log is intended for Vecom Marine's BOILER TREAT ONE SHOT PROGRAMME for low-pressure boilers. It is customised for use with Boiler Treat One Shot, Hydrazide and Condensate Control in conjuction with Test Kit Alkalinity P&M, Test Kit Chloride, Test Kit Oxygen/Hydrazide DEHA and pH Paper 0-14. All recommended limits are for your consideration. Always follow the boiler manufacturer's instructions first.